## Slide 1: Model Calibration

## Slide 2: Initial state

## Slide 3: Manual Calibration – model tuning
Step 1
Exterior wall thermal conductivity x 1.5
Exterior wall thickness x 0.8

## Slide 4: Manual Calibration – model tuning
Step 2
Exterior wall and floor thermal conductivity x 1.5
Exterior wall and floor thickness x 0.8

## Slide 5: Manual Calibration – model tuning
Step 3
Exterior wall and floor thermal conductivity x 2
Exterior wall thickness x 0.8
Exterior glazing U-factor x 1.2
Exterior glazing SHGC x 0.8

## Slide 6: Manual Calibration – model tuning
Step 4
Exterior wall and floor thermal conductivity x 2
Exterior wall thickness x 0.8
Exterior glazing U-factor x 1.2
Exterior glazing SHGC x 0.8
Interior lighting and equipment power density x 1.2

## Slide 7: Manual Calibration – model tuning
Step 5
Exterior wall and floor thermal conductivity x 2
Exterior wall thickness x 0.8
Exterior glazing U-factor x 1.2
Exterior glazing SHGC x 0.8
Interior lighting and equipment power density x 1.1

## Slide 8: Manual Calibration – model tuning
Step 6
Exterior wall and floor thermal conductivity x 2
Exterior wall thickness x 0.8
Exterior glazing U-factor x 1.2
Exterior glazing SHGC x 0.8
Interior lighting and equipment power density x 1.1
Boiler and water heater efficiency x 0.9

## Slide 9: Manual Calibration – model tuning
Step 7
Exterior wall and floor thermal conductivity x 2
Exterior wall thickness x 0.8
Exterior glazing U-factor x 1.2
Exterior glazing SHGC x 0.8
Interior lighting and equipment power density x 1.1
Boiler and water heater efficiency x 0.9
Chiller COP x 0.9

## Slide 10: Manual Calibration – model tuning
Step 8
Exterior wall and floor thermal conductivity x 2
Exterior wall thickness x 0.8
Exterior glazing U-factor x 1.2
Exterior glazing SHGC x 0.8
Interior lighting and equipment power density x 1.1
Boiler and water heater efficiency x 0.9
Chiller COP x 0.9
Occupancy density x 1.5

## Slide 11: Manual Calibration – model tuning
Step 9
Exterior wall and floor thermal conductivity x 2
Exterior wall thickness x 0.8
Exterior glazing U-factor x 1.2
Exterior glazing SHGC x 0.8
Interior lighting and equipment power density x 1.1
Boiler and water heater efficiency x 0.9
Chiller COP x 0.9
Occupancy density x 1.5
Infiltration rate x 1.5

## Slide 12: Manual Calibration – model tuning
Step 10
Exterior wall and floor thermal conductivity x 2
Exterior wall thickness x 0.8
Exterior glazing U-factor x 1.2
Exterior glazing SHGC x 0.8
Interior lighting and equipment power density x 1.1
Boiler and water heater efficiency x 0.9
Chiller COP x 0.9
Occupancy density x 1.5
Infiltration rate x 2

## Slide 13: Manual Calibration – model tuning
Step 11
Exterior wall and floor thermal conductivity x 2
Exterior wall thickness x 0.8
Exterior glazing U-factor x 1.2
Exterior glazing SHGC x 0.8
Interior lighting and equipment power density x 1.1
Boiler and water heater efficiency x 0.9
Chiller COP x 0.9
Occupancy density x 1.5
Infiltration rate x 2
Outdoor air rate per person x 1.5

## Slide 14: Manual Calibration – model tuning
Step 12
Exterior wall and floor thermal conductivity x 2
Exterior wall thickness x 0.8
Exterior glazing U-factor x 1.2
Exterior glazing SHGC x 0.8
Interior lighting and equipment power density x 1.1
Boiler and water heater efficiency x 0.9
Chiller COP x 0.9
Occupancy density x 1.5
Infiltration rate x 2.5
Outdoor air rate per person x 1.5

## Slide 15: Manual Calibration – model tuning
Step 13
Exterior wall and floor thermal conductivity x 2
Exterior wall thickness x 0.8
Exterior glazing U-factor x 1.2
Exterior glazing SHGC x 0.8
Interior lighting and equipment power density x 1.1
Boiler and water heater efficiency x 0.9
Chiller COP x 0.9
Occupancy density x 1.5
Infiltration rate x 2.5
Outdoor air rate per person x 1.3

## Slide 16: Manual Calibration – model tuning
Step 14
Exterior wall and floor thermal conductivity x 2
Exterior wall thickness x 0.8
Exterior glazing U-factor x 1.2
Exterior glazing SHGC x 0.8
Interior lighting and equipment power density x 1.1
Boiler and water heater efficiency x 0.9
Chiller COP x 0.9
Occupancy density x 1.5
Infiltration rate x 2.5
Outdoor air rate per person x 1.4

## Slide 17: Hybrid Calibration – lessons learned
Important: which step to use inverse modeling?
Use it in early steps:
Building and system characteristics are highly uncertain, the inverse solution is meaningless.
The uncertainty of the inverse solution is huge.
Use it in late steps:
The inverse solution is more reliable.
The benefit to monthly calibration precision is marginal.
It benefits more in terms of calibration with high resolution (e.g., hourly, daily)

## Slide 18: Hybrid Calibration – model tuning

## Slide 19: Comparison
Uncalibrated
Calibrated
Target (Ground Truth)

## Slide 20: Comparison
Uncalibrated
Calibrated
Target (Ground Truth)
Hourly gas consumption in heating season

## Slide 21: Manual Calibration – model tuning

## Slide 22: Manual Calibration – model tuning

## Slide 23: Manual Calibration – model tuning