## Slide 1: Model Calibration

## Slide 2: Initial state

## Slide 3: Manual Calibration – model tuning
Step 1
Exterior wall and floor thermal conductivity x 1.5
Exterior wall thickness x 0.8

## Slide 4: Manual Calibration – model tuning
Step 2
Exterior wall and floor thermal conductivity x 2
Exterior wall thickness x 0.8

## Slide 5: Manual Calibration – model tuning
Step 3
Exterior wall and floor thermal conductivity x 2
Exterior wall thickness x 0.8
Interior lighting and equipment power density x 1.5

## Slide 6: Manual Calibration – model tuning
Step 4
Exterior wall and floor thermal conductivity x 2
Exterior wall thickness x 0.8
Interior lighting and equipment power density x 1.2

## Slide 7: Manual Calibration – model tuning
Step 5
Exterior wall and floor thermal conductivity x 2
Exterior wall thickness x 0.8
Interior lighting and equipment power density x 1.1

## Slide 8: Manual Calibration – model tuning
Step 6
Exterior wall and floor thermal conductivity x 2
Exterior wall thickness x 0.8
Interior lighting and equipment power density x 1.1 Boiler and water heater efficiency reduced from 0.78 to 0.75

## Slide 9: Manual Calibration – model tuning
Step 7
Exterior wall and floor thermal conductivity x 2
Exterior wall thickness x 0.8
Interior lighting and equipment power density x 1.1 Boiler and water heater efficiency reduced from 0.75 to 0.7
Notes: Gas consumption still has a huge gap.

## Slide 10: Manual Calibration – model tuning
Step 8
Exterior wall and floor thermal conductivity x 2
Exterior wall thickness x 0.8
Interior lighting and equipment power density x 1.1
Boiler and water heater efficiency reduced from 0.75 to 0.7
Occupancy density x 1.5

## Slide 11: Manual Calibration – model tuning
Step 9
Exterior wall and floor thermal conductivity x 2
Exterior wall thickness x 0.8
Interior lighting and equipment power density x 1.1
Boiler and water heater efficiency reduced from 0.75 to 0.7
Occupancy density x 1.5
Air infiltration rate x 2

## Slide 12: Manual Calibration – model tuning
Step 10
Exterior wall and floor thermal conductivity x 2
Exterior wall thickness x 0.8
Interior lighting and equipment power density x 1.1
Boiler and water heater efficiency reduced from 0.75 to 0.7
Occupancy density x 1.5
Air infiltration rate x 1.5

## Slide 13: Manual Calibration – model tuning
Step 11
Exterior wall and floor thermal conductivity x 2
Floor thermal conductivity x 0.8
Exterior wall thickness x 0.8
Interior lighting and equipment power density x 1.1
Boiler and water heater efficiency reduced from 0.75 to 0.7
Occupancy density x 1.5
Air infiltration rate x 1.5

## Slide 14: Manual Calibration – model tuning
Step 12
Exterior wall and floor thermal conductivity x 2
Floor thermal conductivity x 0.8
Exterior wall thickness x 0.8
Interior lighting and equipment power density x 1.1
Boiler and water heater efficiency reduced from 0.75 to 0.7
Occupancy density x 2
Air infiltration rate x 1.5

## Slide 15: Manual Calibration – model tuning
Step 13
Exterior wall and floor thermal conductivity x 2
Floor thermal conductivity x 0.8
Exterior wall thickness x 0.8
Interior lighting and equipment power density x 1.1
Boiler and water heater efficiency reduced from 0.75 to 0.7
Occupancy density x 3
Air infiltration rate x 1.5

## Slide 16: Manual Calibration – model tuning
Step 14
Exterior wall and floor thermal conductivity x 2
Floor thermal conductivity x 0.8
Exterior wall thickness x 0.8
Interior lighting and equipment power density x 1.1
Boiler and water heater efficiency reduced from 0.75 to 0.7
Occupancy density x 2.7
Air infiltration rate x 1.5

## Slide 17: Hybrid Calibration – model tuning

## Slide 18: Comparison
Uncalibrated
Calibrated
Target (Ground Truth)

## Slide 19: Comparison
Uncalibrated
Calibrated
Target (Ground Truth)
Hourly gas consumption in heating season

## Slide 20: Manual Calibration – model tuning

## Slide 21: Manual Calibration – model tuning

## Slide 22: Manual Calibration – model tuning